## Slide 1: Electrical Safety Program Update
Presenter: Mark Scott
Date: 08/05/16
Electrical Safety

## Slide 2: Research QEW Status
Electrical Safety Committee formed several subcommittees to review and revise requirements for researchers
5 changes expected to better tailor the controls to the hazards

## Slide 3: Proposed Measures for ESP and LOTO
ESP (Chapter 8 and ESM)
Introduce QEW R classification with reduced training
Relax capacitor shock hazard thresholds
LOTO (Chapter 18)
Allow multiple plugs for cord-and-plug LOTO exemption
Simplify conditions for simple LOTO
Introduce Limited LOTO Authorized Person classification with reduced training

## Slide 4: QEW R (Researcher) Classification
QEW Level | Source Type
QEW 1 | 50 – 300 VAC, 50-60 Hz power, provided there is no arc flash hazard
QEW 2 | 50 – 750 VAC, 50-60 Hz power, with or without arc flash hazard
QEW 3 | >750 VAC Utility 60 Hz
QEW R | Other non-line exposure above the thresholds of Table 2.2.13, not otherwise categorized

## Slide 5: QEW R Training
No QEW R Qual Activity managed by AHJ
QEW R will not require PQEW approval
WPC Hazard ELE088 will be modified to match
No 120 VAC work allowed
Training includes:
  CPR/AED
  First Aid
  LOTO (can be waived if C&P only)
  EHS 0538 QEW R Electrical Safety Basics
  Optional modules as required (i.e. capacitors, HVDC, etc.)

## Slide 6: ESM “Table 2.2.13” in Rev 1
Source | Includes | Thresholds
AC | 50-60 Hz nominal | ≥ 50 V and ≥ 5 mA
DC | All | ≥ 100 V and ≥ 40 mA
Capacitors | All | ≥ 100 V and ≥ 10 J
Batteries | Lead-Acid and Lithium Ion | ≥ 100 V
Sub-RF | 1 Hz to 3 kHz (excluding 50-60 Hz nominal) | ≥ 50 V and ≥ 5 mA
RF | 3 kHz to 100 MHz | A function of frequency
Line Hazard
Non-Line Hazards

## Slide 7: Capacitor Threshold raised to 10 Joules
Rev 0 based on 2013 DOE Electrical Safety Handbook:
  100-400V: 1 Joule, >400V: 0.25 Joules
  Initiated by LANL and implemented at ANL, incorporates reflex action hazard
  Not recognized by most other labs in practice
Rev 1 draft based on 1998 DOE Electrical Safety Handbook:
  >100V and >10 Joules
  Circulated at EFCOG Electrical Safety Committee and received wide support
  Mitigates against fibrillation hazard
  Already applied at most labs

## Slide 8: Capacitor Threshold raised to 10 Joules
QEW and written LOTO Procedure required when above new threshold
DOE Handbook thresholds kept for low-hazard electrical control in WPC (non-QEW)
ESM Section 15 (Capacitors) complete rewrite
  Positive response at EFCOG last week, they want to adopt it for the DOE Handbook
  Undergoing review by DC Working Group (Gary Dreifuerst), but initial vetting was already done.

## Slide 9: Cord-and-Plug Exemption
Current policy restricts cord-and-plug exemption to single plug, and multiple plugs trigger a complex LOTO procedure.
Interpretation sought from retired OSHA rep:
  While the language does indicate only one plug, as long as the exclusive control is enforced it should be ok
Most other labs do not enforce single plug rule
Revision to Chapter 18 will remove requirement for single plug and refine definition of exclusive control.
Will be assessed by an ESO on a case-by-case basis at the activity level for R&D applications

## Slide 10: Removal of NFPA 70E requirements for Simple LOTO
OSHA 1910.147
The employer need not document the required procedure for a particular machine or equipment, when all of the following elements exist:
The machine or equipment has no potential for stored or residual energy or reaccumulation of stored energy after shut down which could endanger employees;
The machine or equipment has a single energy source which can be readily identified and isolated;
The isolation and locking out of that energy source will completely deenergize and deactivate the machine or equipment;
The machine or equipment is isolated from that energy source and locked out during servicing or maintenance;
A single lockout device will achieve a locked-out condition;
The lockout device is under the exclusive control of the authorized employee performing the servicing or maintenance;
The servicing or maintenance does not create hazards for other employees; and
In utilizing this exception, there have been no accidents involving the unexpected activation or reenergization of the machine or equipment during servicing or maintenance.
NFPA 70E 120.2(D)
A complex lockout/tagout plan shall be permitted where one or more of the following exist:
Multiple energy sources
Multiple crews
Multiple crafts
Multiple locations
Multiple employers
Multiple disconnecting means
Particular sequences
Job or task that continues for more than one work period
This causes confusion.
Language upheld in 2018 revision
despite multiple attempts to clarify.
Deleting from Chapter 18.

## Slide 11: New LOTO Training Classification
Change proposed by ALS to streamline User LOTO requirements
Adding a shorter LOTO training class for people who only “overlock” on an existing LOTO established by others.
  “Limited LOTO Authorized Person”
Similar to subcontractors and RI’s
  Requires an RI in control of the LOTO and a written LOTO procedure
  Limited LOTO Authorized Person must receive a LOTO briefing
  20 min online training module

## Slide 12: Next Steps
Finalize drafts for Chapter 8, ESM, and Chapter 18
  Note that rev 1 was approved in July but not released for publication.
  Rev 1 will be recirculated for approval after Draft 2 complete.
Modification of WPC hazards, controls and activities
  Migration of QEW 1’s to new activity to match existing non-legacy training
  Examination of remainder and triage to QEW 1 or QEW R
Development of training classes for QEW R and Capacitor Safety
Target rollout in November 2016

## Slide 13: CA 9.1…
Old 9.1
Develop and Implement ESP Training
New 9.1
Develop QEW 1/2 training & certification for EG and FAC
9.2
Finish implementing QEW 1/2 for EG and FAC
9.3
Implement Facilities Subcontractor QEW
9.4
Develop/Implement QEW 3 training & certification
9.7
Finish implementing QEW R/1 for Researchers
9.6
Develop QEW R/1 training and certification for Researchers
9.8
Implement Research Subcontractor QEW
3/1/16
3/1/16
9/30/16
11/30/16
9/30/16
11/30/16
12/30/16
3/31/17
9.5
Develop requirements for Research electrical work
9/30/16
9.9
Develop Non-QEW training
11/30/16
9.10
Implement Non-QEW training
12/31/16
Over the Horizon

## Slide 14: 9.2 – QEW 1/2 Hill Climber (Excludes Research QEW 1)
Chart: 
| Feb | Mar | Apr | May | Jun | Jul | Aug | Sep
QEW 1 Target | 4.5 | 9 | 13.5 | 18 | 22.5 | 27 | 31.5 | 36
QEW 1 | 2 | 6 | 8 | 14 | 23 | 23
QEW 2 Target | 7.75 | 15.5 | 23.25 | 31 | 38.75 | 46.5 | 54.25 | 62
QEW 2 | 3 | 11 | 20 | 26 | 34 | 43

## Slide 15: 9.2 – QEW 1/2 Hill Climber (With Research QEW 1)
Chart: 
| Feb | Mar | Apr | May | Jun | Jul | Aug | Sep
QEW 1 Target | 4.5 | 9 | 13.5 | 18 | 22.5 | 27 | 31.5 | 36
QEW 1 | 2 | 7 | 13 | 20 | 34 | 35
QEW 12
QEW 2 Target | 7.75 | 15.5 | 23.25 | 31 | 38.75 | 46.5 | 54.25 | 62
QEW 2 | 3 | 11 | 20 | 26 | 34 | 43

## Slide 16: Questions?